CHANGES No.1 to TENDER DOSSIER

| Contract Title: | Construction Works of EU–Turkey Anatolian Archaeology and Cultural Heritage Institute |
| --- | --- |
| Publication Reference: | EuropeAid/139911/ID/WKS/TR |

The following alterations and/or corrections are made to the Tender Dossier:

VOLUME 3 TECHNICAL SPECIFICATIONS 6.2. Landscaping Works LW-20: Flag Poles Add new text at the end of section: Length of each flag pole shall be 6 (six) meters LW-25: Construction and installation of ordinary railing with Grade 1 Pitch Pine The item is removed from the technical specifications and scope of works. 8. Special Technical Specifications for Mechanical Works MWHC-01 Floor Type Indoor Unit with Cabin. Cooling capacity (nom): 5.5 kW, heating capacity (nom): 6 kW Add new text at the end of section: All drain pipes shall be PVC DN50 and included in the prices of the units. MWHC-02 Floor-Type Indoor Unit with Cabin. Cooling capacity (nom): 2.8 kW, heating capacity (nom): 3.0 kW Add new text at the end of section: All drain pipes shall be PVC DN50 and included in the prices of the units. MWHC-03 The former text: MWHC-03 Cassette-Type Indoor Unit with Cooling capacity (nom): 7 kW, heating capacity (nom): 7.5 kW This item covers provision and installation of cassette-type interior unit with Cooling capacity (nom): 7 kW (min), heating capacity (nom): 7.5 kW (min), which can be used by mounting in ceiling, delivery in operational condition. Technical information for the unit is given in below table. […] Shall read as new text: MWHC-03 Floor-Type Indoor Unit with Cooling capacity (nom): 7 kW, heating capacity (nom): 7.5 kW This item covers provision, installation, and delivery in working condition of floor-type heating & cooling unit with cabin with Cooling capacity (nom): 7 kW min, heating capacity (nom): 7,5 kW min, which shall be installed on floor. Technical information for the unit is given in below table. All drain pipes shall be PVC DN50 and included in the prices of the units. […] MWHC-04 Outdoor VRV Unit or Group of Units with Cooling capacity (nom): 110 kW, heating capacity (nom): 120 kW Add new text at the end of section: Contractor shall also supply and install lock-in protection for enclosure of Air Conditioner outdoor units. Protection for enclosure shall be made of steel profiles that are welded, bolted and anchored as appropriate. Contractor shall provide related shop drawings for the approval of the Engineer. All drain pipes shall be PVC DN50 and included in the prices of the units. MWSN-04 Squat Toilet (Antibacterial, 50x60 cm extra class with plastic siphon, glass tiled) Add new text at the end of section: Reservoirs of the squat toilets will not be embedded and shall be installed on the adjacent wall. MWSN-16 Disassembly of plumbing and fittings related to Heating Boiler/Fuel Tank Condensate Storage Boiler, Water Pressure Tank The former text: Item covers disassembling, removal, and disposal of the plumbing and fitting materials with welding, that cannot otherwise be disassembled without being damaged, such as heating boiler, fuel tank, boiler, water purification unit. Contractor shall collect, sort as per material types, and stack the removed material on site as per Engineer’s instructions. […] Shall read as new text: Item covers disassembling, removal, and disposal of the plumbing and fitting materials with welding, that cannot otherwise be disassembled without being damaged, such as heating boiler, fuel tank, ventilation shafts, radiators, heating pipes, as well as grey water and clean water pipes. Contractor shall collect, sort as per material types, and stack the removed material on site as per Engineer’s instructions. […] MWSN-22: FM200 Fire Fighting System The former text: […] 2-MINIMUM SYSTEM ARRANGEMENTS Below equipment are listed to provide ONLY MINIMUM requirements. Contractor shall carry out a complete design for the entire building and provide all other additional items to complete and deliver firefighting system operational. HFC 227ea Cylinder 1x61 litres 1 pcs. […] Shall read as new text: […] 2-MINIMUM SYSTEM ARRANGEMENTS Below equipment are listed to provide ONLY MINIMUM requirements. HFC 227ea Cylinder 1x61 litres 1 pcs. […] 10. Special Technical Specifications for Electrical Works EW-101 Lighting pole The former text: Item covers supply and installation of polygonal, galvanized metal lighting poles (type AD1-150/25) as specified below. - Pole material shall be st37 – s235JR as per EN 10025 - Pole shall be hot dip galvanized (EN ISO 1416) - Pole shall be electrostatic oven-dry painted, if requested by the Engineer. - Pole shall be made of one piece up to 12m height. - Pole shall have proper flange for anchoring. - Anchors and screws shall conform with ISO 898.1/5.8 - Poles shall conform with related TEDAŞ regulations. […] Shall read as new text: Item covers supply and installation of polygonal, galvanized metal lighting poles (type AD1-150/25) including lighting fixture as specified below. - Pole material shall be st37 – s235JR as per EN 10025 - Pole shall be hot dip galvanized (EN ISO 1416) - Pole shall be electrostatic oven-dry painted, if requested by the Engineer. - Pole shall be made of one piece up to 12m height. - Pole shall have proper flange for anchoring. - Anchors and screws shall conform with ISO 898.1/5.8 - Poles shall conform with related TEDAŞ regulations. - Lighting Fixture shall be 35W SMD LED having IP 67 electronic driver. […] EW-87 The former text: EW-87; “Energy Cable 4x15mm2 0.6/1kV YVV (NYY) (PVC Insulated, PVC sheathed)” Item covers supply and installation of 4x15mm2 0.6/1kV YVV (NYY) energy cables. Cables shall be PVC insulated and PVC-sheathed. Cables shall be manufactured as per TS IEC 60502-1 and VDE 0276-603. […] Shall read as new text: EW-87; “Energy Cable 4x150mm2 0.6/1kV YVV (NYY) (PVC Insulated, PVC sheathed)” Item covers supply and installation of 4x150mm2 0.6/1kV YVV (NYY) energy cables. Cables shall be PVC insulated and PVC-sheathed. Cables shall be manufactured as per TS IEC 60502-1 and VDE 0276-603. […]

VOLUME 4.3.2 — BILL OF QUANTITIES The former text: PRICE No; TITLE; UNIT; UNIT PRICE; ESTIMATED QUANTITIES; AMOUNT. (a); (b); (c); (d); (e); (f = d * e). LIST-3 MECHANICAL WORKS (Heating & Cooling). […]; […]; […]; […]. MWHC-03; Cassette-Type Indoor Unit with Cooling capacity (nom): 7 kW, heating capacity (nom): 7.5 kW; pcs; 35.00. […]; […]; […]; […]. Shall read as new text: PRICE No; TITLE; UNIT; UNIT PRICE; ESTIMATED QUANTITIES; AMOUNT. (a); (b); (c); (d); (e); (f = d * e). LIST-3 MECHANICAL WORKS (Heating & Cooling). […]; […]; […]; […]. MWHC-03; Floor-Type Indoor Unit with Cooling capacity (nom): 7 kW, heating capacity (nom): 7.5 kW; pcs; 35.00. […]; […]; […]; […]. The former text: PRICE No; TITLE; UNIT; UNIT PRICE; ESTIMATED QUANTITIES; AMOUNT. (a); (b); (c); (d); (e); (f = d * e). LIST-4 ELECTRICAL WORKS. […]; […]; […]; […]. EW-87; Energy Cable 4x15mm2 0.6/1kV YVV (NYY) (PVC Insulated, PVC sheathed); m; 350.00. […]; […]; […]; […]. Shall read as new text: PRICE No; TITLE; UNIT; UNIT PRICE; ESTIMATED QUANTITIES; AMOUNT. (a); (b); (c); (d); (e); (f = d * e). LIST-4 ELECTRICAL WORKS. […]; […]; […]; […]. EW-87; Energy Cable 4x150mm2 0.6/1kV YVV (NYY) (PVC Insulated, PVC sheathed); m; 350.00. […]; […]; […]; […]. The following item is removed from the Bill of Quantities and scope of works. PRICE No; TITLE; UNIT; UNIT PRICE; ESTIMATED QUANTITIES; AMOUNT. (a); (b); (c); (d); (e); (f = d * e). LIST-2 LANDSCAPE WORKS. […]; […]; […]; […]. LW-25; Construction and installation of ordinary railing with Grade 1 Pitch Pine; m2; 172.00. […]; […]; […]; […].

VOLUME 4.3.3 — PRICE SCHEDULE The former text: PRICE No : MWHC-03 Title : Cassette-Type Indoor Unit with Cooling capacity (nom): 7 kW, heating capacity (nom): 7.5 kW. All kind of materials for construction, workshop expenses, vertical and horizontal transportation in the workplace, unloading, workmanship, contractor’s general expenses and profit is included. This price is per pcs. Shall read as new text: PRICE No : MWHC-03 Title : Floor-Type Indoor Unit with Cooling capacity (nom): 7 kW, heating capacity (nom): 7.5 kW. All kind of materials for construction, workshop expenses, vertical and horizontal transportation in the workplace, unloading, workmanship, contractor’s general expenses and profit is included. This price is per pcs. The former text: PRICE No : EW-87 Title : Energy Cable 4x15mm2 0.6/1kV YVV (NYY) (PVC Insulated, PVC sheathed). All kind of materials for construction, workshop expenses, vertical and horizontal transportation in the workplace, unloading, workmanship, contractor’s general expenses and profit is included. This price is per m. Shall read as new text: PRICE No : EW-87 Title : Energy Cable 4x150mm2 0.6/1kV YVV (NYY) (PVC Insulated, PVC sheathed). All kind of materials for construction, workshop expenses, vertical and horizontal transportation in the workplace, unloading, workmanship, contractor’s general expenses and profit is included. This price is per m. The Price Schedule for following item are removed since related work is removed from scope. PRICE No : LW-25 Title : Construction and installation of ordinary railing with Grade 1 Pitch Pine. All kind of materials for construction, workshop expenses, vertical and horizontal transportation in the workplace, unloading, workmanship, contractor’s general expenses and profit is included. This price is per m2.

All other terms and conditions of the Tender Dossier remain unchanged. The above alterations and / or corrections to the tender dossier are an integral part of the Tender Dossier.

***